(IS ARM)

ADVANCED RELAY MODULE

This versatile 1 second to 64 minute ISARMv3 now has a new mode 7 in addition to the previous version’s 6. Timing period potentiometer is replaced by a DIL switch enabling quicker and more accurate time settings. Time range is extended to 64 minutes.

Individual +ve & -ve terminals for trigger and reset eliminate the need for jumper links to select polarity of both.

Auto voltage selection – just connect either 12 or 24volts DC to the power terminals and the ISARMv3 will do the rest.

Operating Modes:

Mode 1	Relay latches on after a trigger 
– requires a reset

Mode 2	Relay on for the timed period 
after a momentary trigger

Mode 3	Relay on whilst trigger is 
present, stays on for timed period after trigger removed, timer resets if trigger re-applied during time period, – thus extending the time period

Mode 4	Relay on after trigger present for more than timed period, off when trigger removed

Mode 5	Relay on whilst trigger is applied for a maximum of the timed period

Mode 6	Timed period starts after trigger is removed, relay on if trigger not re-applied before time out

Mode 7	Momentary trigger, relay on for set time period, off at end of time period. Or if trigger is still present after time period relay on until trigger removed

| Operating Voltage | 10 - 24 Volts DC |
| --- | --- |
| Quiescent Current | 15mA at 12 V 17mA at 24 V |
| Relay Active | 39mA at 12 V 41mA at 24 V |
| Operating Conditions | -10°C to +60°C |
| Trigger and Reset | High: >5 V DC Low: <0.8 V DC |
| Relay Contacts | Min 10mA, Max 8A at 240V AC & 30V DC |
| Supply Input | Reverse polarity protected |
| Dimensions | 56mm (W) 90mm (L) 18mm (H) |
| Packing Weight | 50g |